## Power Utility
Appedix-I: Bill of Materials_Power & Utility_2024
S/L | Description | Specifications | Model/Brand | UoM | Qty | Department/Section | Remark
1 | Portable Airconditioner | Airo Comfort Portable Air Conditioner 14000 BTU |  | Set | 2 | HRAD & Audit Unit
2 | Free Cooling Unit | Free Cooling Unit (Ventilation), 48Volts DC operating system. The controller should be able to control operation between FCU and Air conditioner base on the preset value (Above 18 DegC to 25DegC Ventilaton should operate and when temperature goes above 26DegC AC should start and vice versa) . The set includes additional 3 sets of filters for both Inhouse and exhaust units. | Brand: Icon/BSMC/Equivalent | Sets | 22 | AND
3 | Air Conditioners | 1.5 Ton Split Type, R-32 including mounting brackets/kits for ODU and IDU. The Tubing materials between IDU and ODU should be pure copper. | LG or Equivalent | Sets | 23 | AND
4 | Lighting Bulb | Halogen Bulb, 15Watts, 230-240VAC, Sample can be collected from TICL HQ |  | Nos. | 50 | AND
5 | Lighting Bulb | Halogen Tube, 36 watts, 4 Pins, Sample can be collected from TICL HQ office |  | Nos. | 50 | AND
6 | Socket | Power socket, 16amps with indicator |  | Nos. | 30 | AND
7 | Socket | Power socket, 10amps without indicator |  | Nos. | 30 | AND
8 | CFL Lamp | CFL Lamp, 10 watts, 240VAC |  | Nos. | 40 | AND
9 | Tube Rod | Tube rod Starter |  | Nos. | 150 | AND
10 | Tube Rod | Tube Rod, 1.2m Length, 2650 Lumens, Philips Brand |  | Nos. | 50 | AND
11 | Copper Wire | 4mm2 copper wire(Red) |  | Mts | 270 | AND
12 | Copper Wire | 4mm2 Copper wire(Black) |  | Mts | 270 | AND
13 | Copper Wire | 1.5mm2 Copper wire(Green/Yellow) |  | Mts | 180 | AND
14 | Copper Wire | 2.5mm2 Copper wire(Red) |  | Mts | 270 | AND
15 | Copper Wire | 2.5mm2 Copper wire(Black) |  | Mts | 270 | AND
16 | Insulation Tape | Insulation Tape (Mix Colour) |  | Nos. | 500 | AND
17 | Marking Cloth | Marking cloths |  | Mts | 1000 | AND
18 | Energy Meter Enclosure | Outdoor Type with steel din rail for mounting. | Model# KG9003 Hansel. | Nos. | 12 | SPPD
19 | 2x50sq.mm ABC Cable | 1.1KV, Unarmoured, inner shealthed, 2x50sqmm aluminuim ABC cables, without messenger wire, XLPE insulation, nominal thickness of 1.4mm, Nos of strand 6, minimum inner shealth thickness 0.30mm, nominal outer sheath thickness 2.0mm. The cable should be based on Bhutan Power Corporation (BPC) Standard with product test report (Should have UV test result as well). Each drum should consist of 500m each. |  | Mtrs | 7200 | SPPD | 1mtr sample required
20 | 35sq.mm UG Cable | UG Cable, 35 sq mm, Armored, Aluminium Core, The cable should be based on Bhutan Power Corporation (BPC) Standard with product test report (Should have UV test result as well). Each drum should consist of 500m each. |  | Mtrs | 2400 | SPPD | 1mtr sample required
21 | I-Hook (m16). | I-Hook/Hook bolt for pole, Made of galvanized steel designed for main and service clamp.Fixed length by welded, flat or bended washers. | Brand Preferable : BPC standards | Nos. | 66 | SPPD | 1 No. sample required
22 | Suspension Clamp | Suspension clamp (SPC) for ABC bundle conductor line. Clamp for hanging ABC cable. Cable size 2x (50-150)sq mm | Brand Preferable : BPC standards | Nos. | 180 | SPPD | 2 No. sample required
23 | Dead End Clamp/Low voltage tension clamp. | Tension Clamp for termination of 2 overhead cables. Designed to anchor self supporting LV ABC lines from 2 cores of airdac cable. Cable size=2*(25-50)sq.mm. The item should have the pull out tension of not less than 16KN | Brand Preferable : BPC standards | Nos. | 227 | SPPD | 3 No. sample required
24 | Pole | 7.5m GI Steel Tubular Pole with three 18mm dia holes. Should be Galvanized. |  | Nos. | 48 | SPPD
25 | Stay Set | Stay Set to support electric Pole, Galvanized (Should include Anchor Plate, Anchor Rod, Turn Buckle Bow, Eye Bolt Rod, Stay Set Pole Clamp) | Brand Preferable : BPC standards | Set | 18 | SPPD | 1 set sample required.
26 | Stay Wire | Stay Wire, 16mm for LT, Galvanized, ISO9001 | Brand Preferable : BPC standards | Mtrs | 180 | SPPD | 1 mtr sample required